## Index
Index of spreadsheets
Tracer studies
Water Quality at challenge test
Microbial Challenge Low Flow
Microbial Challenge MS2+E.coli
Microbial Challenge HF(1)
Microbial Challenge HF(2)
Microbial Challenge HF(3)
Microbial Challenge HF(4)
Calc. Ventura Val.
Calc. Low before+high after

## Tracer_studies
				Ventura data:					Seconds
Tracer Studies					1060 L/min Retention time between sampling ports 4 and 5 (seconds) =					18
				355 L/min Retention time between sampling ports 4 and 5 (seconds) =					54
Date	Temperature	Flow (L/min)	Ports	Time after start of rhodamine addition (seconds)	Fluorescence Reading		1060 L/min Retention time between sampling ports 1 and 6 (seconds) =					195
21/04/2015	ambient	285 GPM	1 and 6	0
				10
				20
				30
				40
				50
				60
				70
				80
				90
				100
				110
				120	73.1
				130	69.19
				140	71.09
				150	88.25
				160	73.08
				170	69.67
				180	71.35
				190	70.62
				200	67.71
				210	65.99
				220	64.8
				230	62.87
				240	66.38
				250	82.1
				260	158.4
				270	324.3
				280	451.2
				290	528.9
				300	528.7
				310	547.2
				320	551.1
				330	542.8
				340	552.3
				350	549
				360	542.7
				370	531
				380	450.9
				390	295.3
				400	145.8
				410	98.17
				420	81
				430	71.26
				440	70.82
				450	66.69
				460	66.82
				470	68.14
				480	64.55
				490	69.52
				500	67.16
				510	75.07
21/04/2015	ambient	284 GPM	4 and 5	0	84.72
				10	87.38
				20	83.86
				30	187.7
				40	547.4
				50	597.9
				60	610.8
				70	605.2
				80	606.9
				90	421.8
				100	109.4
				110	93.07
				120	92.46
				130	126.8
				140	90.34
				150	91.31
				160	92.13
				170	89.41
				180	86.09
				190	87.11
				200	86.64
				210	82.21
				220	83.3
				230	84.18
				240	81.09
21/04/2015	ambient	140 GPM	4 and 5	0	69.71
				10	70.58
				20	71.19
				30	72.15
				40	72.09
				50	146
				60	635.9
				70	1017
				80	1117
				90	1140
				100	1145
				110	937.7
				120	536.8
				130	201.7
				140	110.2
				150	86.05
				160	74.21
				170	69.49
				180	68.83
				190	71.78
				200	69.34
				210	69.05
				220	67.84
				230	65.25
				240	64.87

## Water_Quality_at_challenge_test
Water Quality on Challenge Test Days
					On-line			On-line					On-line
Challenge test date	Challenge Test descriptor	Flow tested	Temperratures tested	Alkalinity	pH		Ca	Turbidity	SS	VSS		COD	TOC	EC	UVT
					(mg/L)			(mg/L)			(mg/L)	(uS/cm)
22/04/2015	Low Flow	1065	75, 72,69, 66	36	6.8		17	3.5	13	12		60	13	830	50
24/04/2015	High Flow	355	75, 72,69, 66	60	6.6		16	3.5	16	6		65	14	850	44
27/04/2015	MS2+E,coli	1065	66, 63, 60, 57	42	6.6		16	6.8	24	6		60	15	830	41
27/05/2015	High Flow, Repeat 1	1065	75, 72, 69	59	6.9		18	4.6	24	4		70	15	890	35
2/06/2015	High Flow, Repeat 2	1065	75, 72, 69	43	6.6		16	2.3	16	2		50	13	730	43
23/06/2015	High Flow, Repeat 3	1065	75, 72, 69	53	6.7		17	9	23	33		44	16	830	40

Challenge Test Results

	Test Date
	24/04/2015			27/05/2015					2/06/2015					23/06/2015
Temp.	MS2 count (pfu/mL)	LV	LRV		Average	MS2 count (pfu/mL)	LV	LRV		Average	MS2 count (pfu/mL)	log (count)	LRV		Average	MS2 count (pfu/mL)	log (count)	LRV	Average
(°C)
75	0.3	-0.52	4.5		4.22	1.7	0.23	5.2		5.25	5	0.7	4.7		5.00	1.2	0.08	5.4	5.47
	1	0	4			1.3	0.11	5.3			1.8	0.26	5.2			3	0.48	5
	1	0	4			2	0.3	5.1			7	0.85	4.6			1	0	5.4
	0.2	-0.7	4.7			1	0	5.4			2	0.3	5.1			0.7	-0.15	5.6
	2	0.3	3.7			1	0	5.4			1.5	0.18	5.3			0.3	-0.52	6
	0.4	-0.35	4.4			2	0.3	5.1			2	0.3	5.1			1	0	5.4
72	79	1.9	2.1		2.18	1370	3.14	2.3		2.48	1110	3.05	2.4		2.33	920	2.96	2.5	2.43
	80	1.9	2.1			820	2.91	2.5			1210	3.08	2.4			1150	3.06	2.4
	65	1.81	2.2			1240	3.09	2.3			1190	3.08	2.4			950	2.98	2.5
	50	1.7	2.3			960	2.98	2.5			1380	3.14	2.3			1030	3.01	2.4
	79	1.9	2.1			480	2.68	2.8			1300	3.11	2.3			1020	3.01	2.4
	47	1.67	2.3			950	2.98	2.5			1530	3.18	2.2			1170	3.07	2.4
69	2030	3.31	0.7		0.72	38000	4.58	0.9		0.85	23500	4.37	1.1		1.03	29700	4.47	1	0.98
	1610	3.21	0.8			51000	4.71	0.7			26700	4.43	1			27600	4.44	1
	1930	3.29	0.7			53000	4.72	0.7			23500	4.37	1.1			26500	4.42	1
	1920	3.28	0.7			38000	4.58	0.9			27200	4.43	1			26100	4.42	1
	1980	3.3	0.7			43000	4.63	0.8			24500	4.39	1			28900	4.46	1
	1950	3.29	0.7			21000	4.32	1.1			26800	4.43	1			31300	4.5	0.9

## Microbial_Challenge_Low_Flow
Low flow MS2 challenge tests					Test Conditions
				Time (sec)	Temperaure (F) (=75C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=72C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=69C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=66C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (ambient)	Temperature (C)	Flow (GPM)	Flow (L/min)
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 Count (pfu/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)	LRV		0	167.2	75.2	151	572		0	161.4	71.9	153	579		0	156	68.9	149	564		0	150.9	66.1	151	572		0	77.5	25.3	159	602
22/04/2015	6-75-355-5-1	6	75	355	5	0		0.00		-0.3	0.3	5.3	0.4	5.71625635528303		30	167	75.1	151	572		30	161.7	72.1	153	579		30	156	68.9	152	575		30	150.9	66.1	152	575		30	77.4	25.2	149	564
	6-75-355-5-2					10		0.00					60	167	75.1	150	568		60	161.8	72.2	150	568		60	156.1	69.0	151	572		60	150.9	66.1	151	572		60	77.4	25.2	150	568
	6-75-355-5-3					20		0.00					90	167.1	75.1	151	572		90	161.9	72.2	150	568		90	156	68.9	149	564		90	151	66.2	149	564		90	77.4	25.2	150	568
	6-75-355-5-4					30		0.00					120	167.1	75.1	149	564		120	161.9	72.2	150	568		120	155.9	68.9	151	572		120	150.9	66.1	152	575		120	77.4	25.2	150	568
	6-75-355-5-5					40		0.30	-0.52					150	167.2	75.2	151	572		150	161.9	72.2	150	568		150	156	68.9	150	568		150	150.8	66.1	153	579		150	77.3	25.2	149	564
	6-75-355-5-6					50		0.80	-0.10					180	167.1	75.1	152	575		180	161.8	72.2	151	572		180	156.1	69.0	149	564		180	150.7	66.0	149	564		180	77.3	25.2	150	568
				210	167.1	75.1	152	575		210	161.9	72.2	152	575		210	156.4	69.2	151	572		210	150.6	65.9	153	579		210	77.3	25.2	149	564
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 Count (pfu/mL)	log (count)	Average	SD					240	167	75.1	151	572		240	161.9	72.2	151	572		240	156.3	69.1	150	568		240	150.6	65.9	152	575		240	77.2	25.1	150	568
22/04/2015	7-72-355-5-1	7	72	355	5	0		6	0.78	0.8	0.2	4.1	0.3	4.094891209		270	166.9	75.0	152	575		270	161.8	72.2	151	572		270	156.4	69.2	152	575		270	150.8	66.1	152	575		270	77.2	25.1	149	564
	7-72-355-5-2					10		5	0.70					300	166.9	75.0	151	572		300	161.7	72.1	150	568		300	156.3	69.1	151	572		300	150.9	66.1	153	579		300	77.1	25.1	150	568
	7-72-355-5-3					20		8	0.90					330	166.9	75.0	153	579		330					330					330					330
	7-72-355-5-4					30		4	0.60					360	166.8	74.9	152	575		360					360					360					360
	7-72-355-5-5					40		10	1.00					390	166.9	75.0	151	572		390					390					390					390
	7-72-355-5-6					50		13	1.11					420	167	75.1	152	575		420					420					420					420
				Average		Average				Average		Average				Average		Average				Average		Average				Average		Average
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 Count (pfu/mL)	log (count)	Average	SD					75		573				72		572				69.0		569				66.1		574				25.2		569
22/04/2015	8-69-355-5-1	8	69	355	5	0		1880	3.27	3.3	0.03	1.6	0.2	1.642371449		Feed pump setting (Hz)	not recorded					Feed pump setting (Hz)	not recorded					Feed pump setting (Hz)					Feed pump setting (Hz)	22					Feed pump setting (Hz)	21
	8-69-355-5-2					10		2120	3.33					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)					Effluent Pump position (%)	46					Effluent Pump position (%)	45
	8-69-355-5-3					20		2260	3.35
	8-69-355-5-4					30		2170	3.34					Overall Average Flow
	8-69-355-5-5					40		2290	3.36					571
	8-69-355-5-6					50		2320	3.37					F to C	(F-32) x 0.556
				C to F	(C x 1,8) + 32
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 Count (pfu/mL)	log (count)	Average	SD					GPM to L/min	GPM x 3.785
22/04/2015	9-66-355-5-1	9	66	355	5	0		28000	4.45	4.4	0.2	0.6	0.3	0.593296185
	9-66-355-5-2					10		25000	4.40
	9-66-355-5-3					20		38000	4.58
	9-66-355-5-4					30		23000	4.36
	9-66-355-5-5					40		21000	4.32
	9-66-355-5-6					50		11000	4.04

Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 Count (pfu/mL)	log (count)	Average	SD
22/04/2015	10-amb-355-5-1	10	ambient	355	5	0		139000	5.14	5.0	0.1			4.97949779
	10-amb-355-5-2					10		109000	5.04
	10-amb-355-5-3					20	Triplicate assay	104333	5.02
	10-amb-355-5-4					30		79000	4.90
	10-amb-355-5-5					40		59000	4.77
	10-amb-355-5-6					50		82000	4.91
				Average SD
				0.3

## Microbial_Challenge_MS2+E_coli
Low temp. MS2 Challenge test with assay of native E.Coli					Test Conditions
				Time (sec)	Temperaure (F) (=68C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=64C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=60C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=57C)	Temperature (C)	Flow (GPM)	Flow (L/min)
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time after 14.5 minutes(second)		MS2 counts	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)	E.coli Count (orgs/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)		0	154.2	67.9	287	1086		0	147.1	64.0	290	1098		0	140	60.0	292	1105		0	134.9	57.2	300	1136
24/04/2015	11-57-1065-1-1	11	57	1065	1	0		30000	4.48	4.4546	0.0315	-0.0002	0.0542	57000	4.76	5.0	0.2	0.4	0.27		30	154.3	68.0	289	1094		30	147.3	64.1	296	1120		30	139.8	59.9	289	1094		30	134.9	57.2	301	1139
	11-57-1065-1-2					20		26500	4.42					63000	4.80					60	154.3	68.0	290	1098		60	147.3	64.1	293	1109		60	140	60.0	296	1120		60	135	57.3	292	1105
	11-57-1065-1-3					40		28500	4.45					69000	4.84					90	154.3	68.0	292	1105		90	147.4	64.2	300	1136		90	140	60.0	287	1086		90	134.9	57.2	300	1136
	11-57-1065-1-4					60		28400	4.45					130000	5.11					120	154.5	68.1	288	1090		120	147.5	64.2	285	1079		120	140.1	60.1	291	1101		120	134.8	57.2	294	1113
	11-57-1065-1-5					80		26200	4.42					190000	5.28					150	154.6	68.2	293	1109		150	147.3	64.1	288	1090		150	140.2	60.2	293	1109		150	134.8	57.2	299	1132
	11-57-1065-1-6					100		31700	4.50					91000	4.96					180	154.5	68.1	286	1083		180	147.3	64.1	289	1094		180	140.1	60.1	294	1113		180	134.8	57.2	297	1124
24/04/2015	11-57-1065-6-1	11	57	1065	6	0		27700	4.44	4.4549	0.0227			37000	4.57	4.6	0.1				210	154.6	68.2	291	1101		210	147.2	64.1	291	1101		210	140.1	60.1	288	1090		210	134.6	57.0	292	1105
	11-57-1065-6-2					20		28500	4.45					40000	4.60					240	154.5	68.1	287	1086		240	147.2	64.1	292	1105		240	140	60.0	293	1109		240	134.7	57.1	291	1101
	11-57-1065-6-3					40	Triplicate assay	30800	4.49					39000	4.59					270	154.4	68.1	289	1094		270	147.3	64.1	295	1117		270	139.9	60.0	297	1124		270	134.6	57.0	294	1113
	11-57-1065-6-4					60		26400	4.42					37000	4.57					300	154.3	68.0	286	1083		300	147.5	64.2	293	1109		300	140	60.0	295	1117		300	134.7	57.1	295	1117
	11-57-1065-6-5					80		29400	4.47					35000	4.54					330	154.3	68.0	293	1109		330	147.4	64.2	291	1101		330	140.1	60.1	296	1120		330	134.8	57.2	296	1120
	11-57-1065-6-6					100		28400	4.45					27000	4.43					360	154.4	68.1	292	1105		360	147.4	64.2	295	1117		360	140.1	60.1	291	1101		360	134.9	57.2	299	1132
				390	154.5	68.1	288	1090		390	147.3	64.1	289	1094		390	140.3	60.2	302	1143		390	134.8	57.2	300	1136
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)					E.coli Count (orgs/mL)					420	154.6	68.2	293	1109		420	147.4	64.2	295	1117		420	140.4	60.3	296	1120		420	134.7	57.1	291	1101
24/04/2015	12-60-1065-1-1	12	60	1065	1	0		28600	4.46	4.4095	0.0268	-0.0333	0.0938	87000	4.94	4.9	0.1	0.8	0.15		450	154.7	68.2	291	1101		450	147.2	64.1	298	1128		450	140.4	60.3	301	1139		450	134.6	57.0	300	1136
	12-60-1065-1-2					20		25500	4.41					60000	4.78					480	154.7	68.2	289	1094		480	147.2	64.1	289	1094		480	140.4	60.3	300	1136		480	134.7	57.1	305	1154
	12-60-1065-1-3					40		25800	4.41					120000	5.08					510	154.5	68.1	294	1113		510	147.2	64.1	292	1105		510	140.2	60.2	293	1109		510	134.6	57.0	290	1098
	12-60-1065-1-4					60		24700	4.39					71000	4.85					540	154.4	68.1	286	1083		540	147	63.9	296	1120		540	140.1	60.1	287	1086		540	134.6	57.0	299	1132
	12-60-1065-1-5					80		25900	4.41					83000	4.92					570	154.4	68.1	289	1094		570	147	63.9	298	1128		570	140	60.0	293	1109		570	134.7	57.1	289	1094
	12-60-1065-1-6					100		23800	4.38					100000	5.00					600	154.5	68.1	293	1109		600	147	63.9	293	1109		600	140.1	60.1	291	1101		600	134.7	57.1	286	1083
24/04/2015	12-60-1065-6-1	12	60	1065	6	0		35000	4.54	4.4429	0.0670			13000	4.11	4.1	0.0				630	154.4	68.1	295	1117		630	147.1	64.0	283	1071		630	140.1	60.1	296	1120		630	134.6	57.0	290	1098
	12-60-1065-6-2					20		26000	4.41					15000	4.18					660	154.6	68.2	295	1117		660	147.1	64.0	297	1124		660	140	60.0	301	1139		660	134.6	57.0	290	1098
	12-60-1065-6-3					40		22000	4.34					16000	4.20					690	154.6	68.2	294	1113		690	147.2	64.1	293	1109		690	139.8	59.9	300	1136		690	134.6	57.0	297	1124
	12-60-1065-6-4					60		27000	4.43					13000	4.11					720	154.4	68.1	288	1090		720	147.3	64.1	291	1101		720	139.7	59.9	296	1120		720	134.4	56.9	298	1128
	12-60-1065-6-5					80		28000	4.45					15000	4.18					750	154.3	68.0	296	1120		750	147.2	64.1	292	1105		750	139.7	59.9	286	1083		750	134.4	56.9	303	1147
	12-60-1065-6-6					100		30000	4.48					12000	4.08					780	154.3	68.0	292	1105		780	147.3	64.1	290	1098		780	139.7	59.9	301	1139		780	134.5	57.0	301	1139
				810	154.3	68.0	300	1136		810	147.5	64.2	295	1117		810	139.8	59.9	305	1154		810	134.6	57.0	293	1109
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)					E.coli Count (orgs/mL)					840	154.2	67.9	296	1120		840	147.5	64.2	289	1094		840	140	60.0	296	1120		840	134.7	57.1	289	1094
24/04/2015	13-63-1065-1-1	13	64	1065	1	0		12400	4.09	4.1610	0.0443	-0.0164	0.0859	61000	4.79	4.7	0.0	1.5	0.16		870	154.3	68.0	286	1083		870	147.4	64.2	287	1086		870	140	60.0	295	1117		870	134.7	57.1	292	1105
	13-63-1065-1-2					20		13900	4.14					48000	4.68					900	154.3	68.0	290	1098		900	147.5	64.2	295	1117		900	140	60.0	301	1139		900	134.6	57.0	278	1052
	13-63-1065-1-3					40		15500	4.19					62000	4.79					930	154.3	68.0	291	1101		930	147.4	64.2	291	1101		930	140.1	60.1	292	1105		930	134.7	57.1	294	1113
	13-63-1065-1-4					60		15000	4.18					52000	4.72					960	154.2	67.9	289	1094		960	147.5	64.2	294	1113		960	140.2	60.2	294	1113		960	134.5	57.0	288	1090
	13-63-1065-1-5					80		13900	4.14					61000	4.79					990	154.2	67.9	295	1117		990	147.3	64.1	284	1075		990	140.1	60.1	300	1136		990	134.4	56.9	295	1117
	13-63-1065-1-6					100		16600	4.22					53000	4.72					1020	154.4	68.1	291	1101		1020					1020	139.8	59.9	301	1139		1020
24/04/2015	13-63-1065-6-1	13	64	1065	6	0		16300	4.21	4.1774	0.0417			1600	3.20	3.3	0.1				1050	154.6	68.2	290	1098		1050					1050					1050
	13-63-1065-6-2					20		15200	4.18					1600	3.20					1080	154.6	68.2	300	1136		1080					1080					1080
	13-63-1065-6-3					40		16100	4.21					1700	3.23					Average		Average				Average		Average				Average		Average				Average		Average
	13-63-1065-6-4					60		16100	4.21					1500	3.18					68.1		1102				64.1		1105				60.1		1117				57.1		1115
	13-63-1065-6-5					80		14100	4.15					3100	3.49
	13-63-1065-6-6					100		12800	4.11					2000	3.30
				Feed pump setting (Hz)	not recorded					Feed pump setting (Hz)	35					Feed pump setting (Hz)	35					Feed pump setting (Hz)	35
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)					E.coli Count (orgs/mL)					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)					Effluent Pump position (%)				Overall Average Flow
24/04/2015	14-66-1065-1-1	14	68	1065	1	0		14100	4.15	4.1351	0.0343	0.7611	0.2161	68000	4.83	4.8	0.1	2.9	0.33					1188
	14-66-1065-1-2					20		12000	4.08					63000	4.80
	14-66-1065-1-3					40		13600	4.13					65000	4.81
	14-66-1065-1-4					60		14600	4.16					57000	4.76
	14-66-1065-1-5					80		13000	4.11					50000	4.70
	14-66-1065-1-6					100		14800	4.17					49000	4.69
24/04/2015	14-66-1065-6-1	14	68	1065	6	0		1400	3.15	3.3740	0.1818			88	1.94	1.9	0.3
	14-66-1065-6-2					20		2200	3.34					120	2.08
	14-66-1065-6-3					40		1700	3.23					22	1.34
	14-66-1065-6-4					60		3100	3.49					75	1.88
	14-66-1065-6-5					80		4500	3.65					98	1.99
	14-66-1065-6-6					100		2400	3.38					110	2.04
				Average SD					Average SD
				0.11					0.23

## Microbial_Challenge_HF(1)
High Flow Challenge Test 1					Paul's
				Calculation	Test Conditions
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)	LRV	Time (sec)	Temperaure (F) (=75C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=72C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=69C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=66C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (ambient)	Temperature (C)	Flow (GPM)	Flow (L/min)
24/04/2015	1-75-1065-5-1	1	75	1065	5	0		0.3	-0.52	-0.2	0.4	4.2	0.5	4.114316303	0	166.9	75.0	290	1098		0	161.7	72.1	292	1105		0	156.2	69.1	293	1109		0	150.8	66.1	283	1071		0	84	28.9	286	1083
	1-75-1065-5-2					10		1.0	0.00					30	166.9	75.0	288	1090		30	161.6	72.1	292	1105		30	156.1	69.0	289	1094		30	150.8	66.1	291	1101		30	83.9	28.9	284	1075
	1-75-1065-5-3					20		1.0	0.00					60	166.8	74.9	284	1075		60	161.7	72.1	295	1117		60	156.2	69.1	291	1101		60	150.9	66.1	286	1083		60	83.9	28.9	287	1086
	1-75-1065-5-4					30		0.2	-0.70					90	166.8	74.9	287	1086		90	161.7	72.1	291	1101		90	156.2	69.1	293	1109		90	150.7	66.0	284	1075		90	83.5	28.6	285	1079
	1-75-1065-5-5					40		2.0	0.30					120	166.7	74.9	286	1083		120	161.7	72.1	293	1109		120	156.1	69.0	293	1109		120	150.8	66.1	291	1101		120	83.4	28.6	287	1086
	1-75-1065-5-6					50		0.4	-0.35					150	166.7	74.9	292	1105		150	161.7	72.1	294	1113		150	156.3	69.1	287	1086		150	150.8	66.1	290	1098		150	83.3	28.5	287	1086
				180	166.8	74.9	284	1075		180	161.6	72.1	291	1101		180	156.1	69.0	284	1075		180	150.9	66.1	287	1086		180	83.3	28.5	286	1083
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average	SD				210	166.9	75.0	294	1113		210	161.5	72.0	293	1109		210	156.3	69.1	287	1086		210	150.9	66.1	285	1079		210	83.1	28.4	284	1075
24/04/2015	2-72-1065-5-1	2	72	1065	5	0		79	1.90	1.8	0.1	2.2	0.2	2.206373813	240	167	75.1	294	1113		240					240					240					240
	2-72-1065-5-2					10		80	1.90					270					270					270					270					270
	2-72-1065-5-3					20		65	1.81					300		Average		Average		300		Average		Average		300		Average		Average		300		Average		Average		300		Average		Average
	2-72-1065-5-4					30		50	1.70					330		75.0		1093		330		72.1		1108		330		69.0		1096		330		66.1		1087		330		28.7		1082
	2-72-1065-5-5					40		79	1.90					360		SD		SD		360		SD		SD		360		SD		SD		360		SD		SD		360		SD		SD
	2-72-1065-5-6					50		47	1.67					390		0.0556		14.87483062		390		0.042029649		5.328848333		390		0.046399477		12.94471581		390		0.039315137		12.04379625		390		0.187962306		4.85138548
				420					420					420					420					420
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average	SD					1093
24/04/2015	3-69-1065-5-1	3	69	1065	5	0		2030	3.31	3.3	0.04	0.7	0.1	0.7507677	Feed pump setting (Hz)	not recorded					Feed pump setting (Hz)	not recorded					Feed pump setting (Hz)					Feed pump setting (Hz)	22					Feed pump setting (Hz)	21
	3-69-1065-5-2					10		1610	3.21					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)	nor recorded					Effluent Pump position (%)					Effluent Pump position (%)	46					Effluent Pump position (%)	45
	3-69-1065-5-3					20		1930	3.29
	3-69-1065-5-4					30		1920	3.28
	3-69-1065-5-5					40		1980	3.30
	3-69-1065-5-6					50		1950	3.29

Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average	SD
24/04/2015	4-66-1065-5-1	4	66	1065	5	0		2800	3.45	3.2	0.2	0.8	0.3	0.791400465
	4-66-1065-5-2					10		2100	3.32
	4-66-1065-5-3					20		1500	3.18
	4-66-1065-5-4					30		1600	3.20
	4-66-1065-5-5					40		1000	3.00
	4-66-1065-5-6					50		1400	3.15

Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average	SD			LV
24/04/2015	5-amb-1065-5-1	5	ambient	1065	5	0		7300	3.86	4.0	0.1			4.030282554
	5-amb-1065-5-2					10		10900	4.04
	5-amb-1065-5-3					20	Triplicate assay	11133	4.05
	5-amb-1065-5-4					30		9400	3.97
	5-amb-1065-5-5					40		10900	4.04
	5-amb-1065-5-6					50		14700	4.17
				Average SD
				0.3

				27-05-15 results
				75	5.258743675

				72	2.4480632

				69	0.825596358

## Microbial_Challenge_HF(2)
High Flow Challenge Test 2
					Test Conditions
Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)		Time (sec)	Temperaure (F) (=75C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=72C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=69C)	Temperature (C)	Flow (GPM)	Flow (L/min)		Time (sec)	Temperaure (F) (=66C)	Temperature (C)	Flow (GPM)	Flow (L/min)
27/05/2015	15-75-1065-5-1	15	75	1065	5	0		1.7	0.23	0.2	0.2	5.3	0.2		0	167.1	75.1	277	1048		0	162.4	72.5	287	1086		0	156.2	69.1	286	1083		0	84.6	29.2	281	1064
	15-75-1065-5-2					30		1.3	0.11					30	167.1	75.1	281	1064		30	162.1	72.3	286	1083		30	156.2	69.1	287	1086		30	84.3	29.1	278	1052
	15-75-1065-5-3					60		2.0	0.30					60	166.9	75.0	275	1041		60	162	72.3	288	1090		60	155.9	68.9	281	1064		60	84.2	29.0	279	1056
	15-75-1065-5-4					90		1.0	0.00					90	166.8	74.9	288	1090		90	161.8	72.2	281	1064		90	155.8	68.8	284	1075		90	84.1	29.0	278	1052
	15-75-1065-5-5					120		1.0	0.00					120	166.6	74.8	286	1083		120	161.9	72.2	282	1067		120	157.7	69.9	277	1048		120	83.9	28.9	280	1060
	15-75-1065-5-6					150		2.0	0.30					150	166.7	74.9	287	1086		150	161.8	72.2	287	1086		150	155.8	68.8	288	1090		150	83.8	28.8	279	1056
	15-75-1065-5-7					180	166.7	74.9	288	1090		180	161.7	72.1	283	1071		180	156	68.9	281	1064		180	83.6	28.7	277	1048
	15-75-1065-5-8					log (count)	Average	SD				210	166.4	74.7	287	1086		210	161.8	72.2	282	1067		210	156.3	69.1	286	1083		210	83.3	28.5	275	1041
27/05/2015	16-72-1065-5-1	16	72	1065	5	0		1370	3.14	3.0	0.2	2.5	0.2		240					240					240	155.8	68.8	289	1094		240	83	28.4	275	1041
	16-72-1065-5-2					30		820	2.91					270					270					270					270
	16-72-1065-5-3					60		1240	3.09					300		Average		Average		300		Average		Average		300		Average		Average		300		Average		Average
	16-72-1065-5-4					90		960	2.98					330		74.9		1074		330		72.2		1077		330		69.0		1076		330		28.8		1052
	16-72-1065-5-5					120		480	2.68					360		SD		SD		360		SD		SD		360		SD		SD		360		SD		SD
	16-72-1065-5-6					150		950	2.98					390		0.134355254		19.81645933		390		0.125869853		10.51268723		390		0.33295586		14.9015599		390		0.280766237		7.802977396
	16-69-1065-5-7					420					420					420					420
	16-69-1065-5-8					log (count)	Average	SD
27/05/2015	17-69-1065-5-1	17	69	1065	5	0		38000	4.58	4.6	0.15	0.8	0.2
	17-69-1065-5-2					30		51000	4.71
	17-69-1065-5-3					60		53000	4.72
	17-69-1065-5-4					90		38000	4.58
	17-69-1065-5-5					120		43000	4.63
	17-69-1065-5-6					150		21000	4.32
	17-69-1065-5-7
	17-69-1065-5-8					log (count)	Average	SD
27/05/2015	18-amb-1065-5-1	18	ambient	1065	5	0		253000	5.40	5.4	0.0
	18-amb-1065-5-2					30		266000	5.42
	18-amb-1065-5-3					60	Triplicate assay	264000	5.42
	18-amb-1065-5-4					90		270000	5.43
	18-amb-1065-5-5					120		269000	5.43
	18-amb-1065-5-6					150		311000	5.49
	18-amb-1065-5-7
	18-amb-1065-5-8
					Average SD
					0.2

## Microbial_Challenge_HF(3)
High Flow Challenge Test 3

Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)
2/06/2015	19-75-1065-5-1	19	75	1065	5	0		5.0	0.70	0.4	0.3	5.0	0.3
	19-75-1065-5-2					30		1.8	0.26
	19-75-1065-5-3					60		7.0	0.85
	19-75-1065-5-4					90		2.0	0.30
	19-75-1065-5-5					120		1.5	0.18
	19-75-1065-5-6					150		2.0	0.30
	19-75-1065-5-7					180
	19-75-1065-5-8					210			log (count)	Average	SD
2/06/2015	20-72-1065-5-1	20	72	1065	5	0		1110	3.05	3.1	0.1	2.3	0.1
	20-72-1065-5-2					30		1210	3.08
	20-72-1065-5-3					60		1190	3.08
	20-72-1065-5-4					90		1380	3.14
	20-72-1065-5-5					120		1300	3.11
	20-72-1065-5-6					150		1530	3.18
	20-72-1065-5-7
	20-72-1065-5-8					log (count)	Average	SD
2/06/2015	21-69-1065-5-1	21	69	1065	5	0		23500	4.37	4.4	0.03	1.0	0.1
	21-69-1065-5-2					30		26700	4.43
	21-69-1065-5-3					60		23500	4.37
	21-69-1065-5-4					90		27200	4.43
	21-69-1065-5-5					120		24500	4.39
	21-69-1065-5-6					150		26800	4.43
	21-69-1065-5-7					180
	21-69-1065-5-8					210			log (count)	Average	SD
2/06/2015	22-amb-1065-5-1	22	ambient	1065	5	0		246000	5.39	5.4	0.0
	22-amb-1065-5-2					30		272000	5.43
	22-amb-1065-5-3					60	Triplicate assay	274000	5.44
	22-amb-1065-5-4					90		248000	5.39
	22-amb-1065-5-5					120		272000	5.43
	22-amb-1065-5-6					150		277000	5.44
	22-amb-1065-5-7					180
	22-amb-1065-5-8					210
					Average SD
					0.1

## Microbial_Challenge_HF(4)
High Flow Challenge Test 4

Sample Date	Sample No.	Challenge Test No	Temperature (Deg.C)	Flow Rate (L/min)	Sample Port	Sample time (second)		MS2 count (pfu/mL)	log (count)	Average (Log (count))	SD (log(count))	LRV	SD (LRV)
23/06/2015	23-75-1065-5-1	23	75	1065	5	0		1.2	0.08	-0.02	0.33	5.48	0.35
	23-75-1065-5-2					30		3	0.48
	23-75-1065-5-3					60		1	0.00
	23-75-1065-5-4					90		0.7	-0.15
	23-75-1065-5-5					120		0.3	-0.52
	23-75-1065-5-6					150		1	0.00
23/06/2015	24-72-1065-5-1	24	72	1065	5	0
	24-72-1065-5-2					30			log (count)	Average	SD
	24-72-1065-5-3					60		920	2.96	3.02	0.04	2.44	0.06
	24-72-1065-5-4					90		1150	3.06
	24-72-1065-5-5					120		950	2.98
	24-72-1065-5-6					150		1030	3.01
23/06/2015	25-69-1065-5-1	25	69	1065	5	0		1020	3.01
	25-69-1065-5-2					30		1170	3.07
	25-69-1065-5-3					60
	25-69-1065-5-4					90			log (count)	Average	SD
	25-69-1065-5-5					120		29700	4.47	4.45	0.03	1.00	0.05
	25-69-1065-5-6					150		27600	4.44
23/06/2015	26-amb-1065-5-1	26	Ambient	1065	5	0		26500	4.42
	26-amb-1065-5-2					30		26100	4.42
	26-amb-1065-5-3					60	Triplicate assay	28900	4.46
	26-amb-1065-5-4					90		31300	4.50
	26-amb-1065-5-5					120
	26-amb-1065-5-6					150			log (count)	Average	SD
					298000	5.47	5.46	0.02
					260000	5.41
					292333	5.47
					288000	5.46
					284000	5.45
					294000	5.47

					Average SD
					0.2

## Calc__Ventura_Val_
Pooled Data					Temperature
24/04/2015					27/05/2015				2/06/2015				23/06/2015				Test Date	75	72	69
Temp ( C )	MS2 count (pfu/mL)	log (count)	LRV		MS2 count (pfu/mL)	log (count)	LRV		MS2 count (pfu/mL)	log (count)	LRV		MS2 count (pfu/mL)	log (count)	LRV		24/04/2015	4.5	2.1	0.7
75	0.3	-0.52	4.5		1.7	0.23	5.2		5.0	0.70	4.7		1.2	0.08	5.4			4.0	2.1	0.8
	1.0	0.00	4.0		1.3	0.11	5.3		1.8	0.26	5.2		3.0	0.48	5.0			4.0	2.2	0.7
	1.0	0.00	4.0		2.0	0.30	5.1		7.0	0.85	4.6		1.0	0.00	5.4			4.7	2.3	0.7
	0.2	-0.70	4.7		1.0	0.00	5.4		2.0	0.30	5.1		0.7	-0.15	5.6			3.7	2.1	0.7
	2.0	0.30	3.7		1.0	0.00	5.4		1.5	0.18	5.3		0.3	-0.52	6.0			4.4	2.3	0.7
	0.4	-0.35	4.4		2.0	0.30	5.1		2.0	0.30	5.1		1.0	0.00	5.4		27/05/2015	5.2	2.3	0.9
				5.3	2.5	0.7
				5.1	2.3	0.7
72	79	1.90	2.1		1370	3.14	2.3		1110	3.05	2.4		920	2.96	2.5			5.4	2.5	0.9
	80	1.90	2.1		820	2.91	2.5		1210	3.08	2.4		1150	3.06	2.4			5.4	2.8	0.8
	65	1.81	2.2		1240	3.09	2.3		1190	3.08	2.4		950	2.98	2.5			5.1	2.5	1.1
	50	1.70	2.3		960	2.98	2.5		1380	3.14	2.3		1030	3.01	2.4		2/06/2015	4.7	2.4	1.1
	79	1.90	2.1		480	2.68	2.8		1300	3.11	2.3		1020	3.01	2.4			5.2	2.4	1.0
	47	1.67	2.3		950	2.98	2.5		1530	3.18	2.2		1170	3.07	2.4			4.6	2.4	1.1
				5.1	2.3	1.0
				5.3	2.3	1.0
69	2030	3.31	0.7		38000	4.58	0.9		23500	4.37	1.1		29700	4.47	1.0			5.1	2.2	1.0
	1610	3.21	0.8		51000	4.71	0.7		26700	4.43	1.0		27600	4.44	1.0		23/06/2015	5.4	2.5	1.0
	1930	3.29	0.7		53000	4.72	0.7		23500	4.37	1.1		26500	4.42	1.0			5.0	2.4	1.0
	1920	3.28	0.7		38000	4.58	0.9		27200	4.43	1.0		26100	4.42	1.0			5.4	2.5	1.0
	1980	3.30	0.7		43000	4.63	0.8		24500	4.39	1.0		28900	4.46	1.0			5.6	2.4	1.0
	1950	3.29	0.7		21000	4.32	1.1		26800	4.43	1.0		31300	4.50	0.9			6.0	2.4	1.0
				5.4	2.4	0.9

66	2800	3.45	0.6					Average LRV	5.0	2.4	0.9
	2100	3.32	0.7					SD	0.5	0.1	0.1	Average SD	0.3
	1500	3.18	0.8					Bottom 5th percentile LRV	4.0	2.1	0.7
	1600	3.20	0.8
	1000	3.00	1.0
	1400	3.15	0.9

	MS2 count (pfu/mL)	log (count)	Average(log(count))			log (count)	Average(log(count))			log (count)	Average(log(count))			log (count)	Average(log(count))
Ambient	7300	3.86	4.0		253000	5.40	5.4		246000	5.39	5.4		298000	5.47	5.5
	10900	4.04			266000	5.42			272000	5.43			260000	5.41
	11133	4.05			264000	5.42			274000	5.44			292333	5.47
	9400	3.97			270000	5.43			248000	5.39			288000	5.46
	10900	4.04			269000	5.43			272000	5.43			284000	5.45
	14700	4.17			311000	5.49			277000	5.44			294000	5.47

## Calc__Low_before+high_after
Pooled Data
	24/04/2015			27/05/2015			2/06/2015			23/06/2015
Temp (C)	MS2 count (pfu/mL)	log (count)		MS2 count (pfu/mL)	log (count)		MS2 count (pfu/mL)	log (count)		MS2 count (pfu/mL)	log (count)			75C	72C	69C	Ambient
75	0.3	-0.52		1.7	0.23		5.0	0.70		1.2	0.08		24/04/2015	-0.5	1.9	3.3	3.9
	1.0	0.00		1.3	0.11		1.8	0.26		3.0	0.48			0.0	1.9	3.2	4.0
	1.0	0.00		2.0	0.30		7.0	0.85		1.0	0.00			0.0	1.8	3.3	4.0
	0.2	-0.70		1.0	0.00		2.0	0.30		0.7	-0.15			-0.7	1.7	3.3	4.0
	2.0	0.30		1.0	0.00		1.5	0.18		0.3	-0.52			0.3	1.9	3.3	4.0
	0.4	-0.35		2.0	0.30		2.0	0.30		1.0	0.00			-0.4	1.7	3.3	4.2
					27/05/2015	0.2	3.1	4.6	5.4
					0.1	2.9	4.7	5.4
72	79	1.90		1370	3.14		1110	3.05		920	2.96			0.3	3.1	4.7	5.4
	80	1.90		820	2.91		1210	3.08		1150	3.06			0.0	3.0	4.6	5.4
	65	1.81		1240	3.09		1190	3.08		950	2.98			0.0	2.7	4.6	5.4
	50	1.70		960	2.98		1380	3.14		1030	3.01			0.3	3.0	4.3	5.5
	79	1.90		480	2.68		1300	3.11		1020	3.01		2/06/2015	0.7	3.0	4.4	5.4
	47	1.67		950	2.98		1530	3.18		1170	3.07			0.3	3.1	4.4	5.4
					0.8	3.1	4.4	5.4
					0.3	3.1	4.4	5.4
69	2030	3.31		38000	4.58		23500	4.37		29700	4.47			0.2	3.1	4.4	5.4
	1610	3.21		51000	4.71		26700	4.43		27600	4.44			0.3	3.2	4.4	5.4
	1930	3.29		53000	4.72		23500	4.37		26500	4.42		23/06/2015	0.08	3.0	4.5	5.47
	1920	3.28		38000	4.58		27200	4.43		26100	4.42			0.477121255	3.1	4.4	5.41
	1980	3.30		43000	4.63		24500	4.39		28900	4.46			0	3.0	4.4	5.47
	1950	3.29		21000	4.32		26800	4.43		31300	4.50			-0.15490196	3.0	4.4	5.46
					-0.522878745	3.0	4.5	5.45
	MS2 count (pfu/mL)	log (count)					0	3.1	4.5	5.47
66	2800	3.45
	2100	3.32					Average LV	0.1	2.7	4.2	5.1
	1500	3.18					SD	0.4	0.5	0.5	0.6
	1600	3.20					Average LRV	5.0	2.4	0.9
	1000	3.00
	1400	3.15					Top 5th percentile LV	0.7	3.1	4.7
					Bottom 5th percentile LV				4.0
	MS2 count (pfu/mL)	log (count)			log (count)			log (count)			log (count)		Bottom 5th percentile LRV	3.3	0.8	-0.7
Ambient	7300	3.86		253000	5.40		246000	5.39		298000	5.47
	10900	4.04		266000	5.42		272000	5.43		260000	5.41
	11133	4.05		264000	5.42		274000	5.44		292333	5.47
	9400	3.97		270000	5.43		248000	5.39		288000	5.46
	10900	4.04		269000	5.43		272000	5.43		284000	5.45
	14700	4.17		311000	5.49		277000	5.44		294000	5.47